## Sheet 1
HOME UPS Specification
S. No. | Parameter | Unit | Rating
1 | Model name |  | Smart Home 900 |  | Smart Home 1100 | Smart Home 1400
2 | System rating (Name Plate) | kVA | 700 |  | 900 | 1100
3 | Full Load Input Current ±2A | Amp | 45 |  | 55 | 65
4 | Operating DC voltage | V | 12
5 | Switching element in Inverter |  | MOSFET
6 | Type of Control |  | PWM
7 | Nominal Output voltage in inverter mode | Vac | 220V ± 7V
8 | Output supply phases |  | single
9 | Nominal Output Frequency of Inverter | Hz | 50/60 ± 1 (Default is 50Hz) selectable 50/60Hz (Optional
10 | Frequency (Min - Max during Grid by pass) UPS mode | Hz | 47-53/57-63
11 | Frequency (Min - Max during Grid by pass) Inverter mode | Hz | 40-60/50-70
12 | Output voltage regulation | % | 180-220
13 | Output THD (v) at linear load | % | <5%
14 | Crest Factor |  | 3:01
15 | Overload capacity 125% | Sec | 6 (6 Retry)
16 | Overload capacity 150% | Sec | 2 (6 Retry)
17 | Cooling Fan ON at temp | ⁰C | 60 (or 45% of rated Load)
18 | Cooling Fan Off at temp | ⁰C | 55 (or 40% of rated Load)
19 | Peak efficiency of inverter | % | 82 |  | 82 | 81
20 | Battery low voltage alarm per battery | Vdc | 10.8 ± 0.2
21 | Battery low voltage cut per battery | Vdc | 10.5 ± 0.1 (With 4 Retry)
22 | Max Battery charging voltage by grid per battery | Vdc | 14.4 ± 0.2 settable for Tub-14.4V/28.8V, GEL-14.2V/28.4V, SMF-14.2V/28.4, Flat-14.2V/28.4V settable for Tub-13.8V/27.6V, GEL-13.8V/27.6V, SMF-13.8V/27.6, Flat-13.6V/27.2V
23 | Max Battery charging current by grid in Hi/Lo option | Adc | 12/9 ±2A settable for Tub- 12/9A,GEL- 12/8A, SMF- 11/8A, Flat-11/8 | 16/12 ±2A settable for Tub-16/12A, GEL-16/10A, SMF-14/10A, Flat-14/10
24 | Battery High cut with Alarm per battery | Vdc | 14.8±0.2
25 | Battery High cut Recovery per battery | Vdc | 14.3±0.2
26 | Grid low cut voltage (IT load/Normal load) | Vac | 180/100 ± 10
27 | Grid low cut voltage recovery (IT load/Normal load | Vac | 190/110 ± 10
28 | Grid high cut voltage (IT load/Normal load) | Vac | 265/280 ± 10
29 | Grid high cut voltage recovery (IT load/Normal load | Vac | 255/270 ± 10
30 | Grid charging Enable/Disable |  | yes
31 | Selection of UPS Load/Normal Load |  | yes
32 | Output Voltage at No load at rated Battery voltage | Vac | 220
33 | Output Voltage at 100% load at Nominal Battery voltage | Vac | 208 |  | 208 | 203
34 | Input current at no load at Nominal Battery voltage | Adc | 2.2 |  | 2.6 | 2.4

## Table 2
52 | Noise @ 1 meter | dB | <50
53 | Protections |  | Overload, Battery Deep discharge, Battery Overcharge, Short circuit(1retry),Battery Hi,Over Temp,Fuse Trip, battery reverse
54 | LCD Display parameters |  | Battery voltage, Mains voltage, UPS ON/OFF, UPS Mode, Load percentage (0 to 110%), over load, short ckt, fault, battery low, over temp,Fuse trip, (Customized LCD )
55 | Indication LEDs |  | Tact switch Status
56 | Operating Temperature range | ⁰C | 0-50
57 | Storage Temperature range | ⁰C | 0 +65
58 | Max RH | % | 95
59 | Front panel details ( MCB, Display, Selection switch etc |  | Display with tact switch
60 | Rear panel details (MCB, Terminals etc) |  | O/P socket, fuse/Circuit breaker, mains & batt. Cable and fan, Termina
61 | Enclosure protection |  | 20
62 | Changeover time from inverter to mains in UPS mode | ms | <10
63 | Changeover time from inverter to mains in Normal mode | ms | <10
64 | Changeover time from mains to inverter in UPS mode | ms | <10
65 | Changeover time from mains to inverter in Normal mode | ms | <40
66 | Battery connection |  | thru Copper cable 4 sqmm and 1mtr red 0.7mtr black length | thru Copper cable 10 sqmm and 1mtr red 0.7mtr black length | thru Copper cable 16 sqmm and 1mtr red 0.8mtr black length | thru Copper cable 25 sqmm and 1.25mtr red 1mtr black length | thru Copper cable 10 sqmm and 1.25mtr red 1mtr black length | thru Copper cable 16 sqmm and 1.25mtr red 1mtr black length | thru Copper cable 16 sqmm and 1.25mtr red 1mtr black length
67 | Mains connection |  | 3 core copper cable size 0.75sqmm, 1 .5mtr length with TOP |  |  |  |  | 3 core copper cable size 1.5sqmm, 1 .5mtr length with TOP | 3 core copper cable size 1.5sqmm, 1 .5mtr length with TOP
68 | Output |  | 3pin socket 16A |  |  |  |  | Terminal 30A | Terminal 30A
69 | MCB in battery path |  | NA
70 | Fuse in battery path |  | Internal Fuse
72 | Grid By pass Manually |  | Through switch
73 | Input Protection |  | Resettable Circuit breaker
75 | Front panel Switch Detail
1 | Charging Current Low High Setting
1A. On Pressing "SET" button once - Charging Current present Setting will be displayed.

## Table 3
1B. While "Charging Current" setting is displayed, pressing the "CHANGE" button will alternate between the available charging current options. Charging current will have two options "LO" and "HI" as displayed above.Default value "HI".
2 | Battery Selection
2A. On pressing "SET" button again, selected "BATTERY TYPE" will be displayed.
2B. The "BATTERY TYPE" selection will have four options - TUB (Tubular Battery), FLT (Flat Plate Battery), SF (SMF or VRLA Battery), GEL (Tubular Gel battery). While the selected battery type is displayed, on pressing "CHANGE" button will alternate between the four available options in the order listed above.Default value "TUB".
3 | Grid Charging Mode Enable/Disable
3A. On Pressing "SET" button once - Grid Charging Enable/Disable present Setting will be displayed.
3B. While "Grid Charging Mode" setting is displayed, pressing the "CHANGE" button will alternate between the available charging mode options. Charging mode will have two options "GCE(Grid Charging Enable)" and "GCD(Grid Charging Disable)" as displayed above.Default value "GCE".
4 | UPS / INVERTER Mode Selection
4A. On Pressing "SET" button once - UPS/Inverter present Setting will be displayed.
4B. While "UPS/INVERTER MODE" setting is displayed, pressing the "CHANGE" button will alternate between the available Setting options. UPS/Inverter will have two options "UPD" ( UPS Mode Disable) and "UPE" (UPS Mode Enable) as displayed per battery above.Default Selection is "UPD".

## Table 6
Note: RESET Switch - If Switch is press for 5Sec and release after beep sound then the all setting wil be resetted to default value